SPECIFICATIONS                                                                                                                                CircuitSolver®

Thermostatic Balance Valve

. . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . . .

# SECTION 22 11 19

Domestic Water Piping Specialties

PART 1 GENERAL

1.01       SECTION INCLUDES

# Unit shall be a CircuitSolver® Thermostatic Balance Valve Models CS, CSU, CSUA, CSUA-PT CSUAS, CSUAS-PT, or CSUTD-D as manufactured by ThermOmegaTech.

# Furnish Thermostatic Balance Valve with capabilities as indicated in the plans.

1.02       RELATED SECTIONS

- Section 22 11 00 – Facility Water Distribution

- Section 22 11 16 – Domestic Water Piping

1.03       REFERENCES

- ANSI - American National Standards Institute

- ISO - International Standards Organization

- NSF – National Science Foundation

1.04       SUBMITTALS

- CS, CSU, CSUA, CSUA-PT, CSUAS, CSUAS-PT, & CSUTD-D submittals

- Technical Brochure

- Dimensional prints

- Sales Brochure

1.05      QUALITY ASSURANCE

- The valve manufacturer shall be fully certified by the International Standards Organization per ISO 9001:2015.

- The valve shall be NSF61 certified.

- The valve shall carry a 10-year warranty.

1.06      MAINTENANCE MATERIAL SUBMITTALS

- Installation & maintenance instruction manual

PART 2 PRODUCTS

2.01      MANUFACTURERS

# Subject to compliance with these specifications, the following manufacturers shall be acceptable:

- Thermostatic Balance Valve

- ThermOmegaTech Inc. CircuitSolver® Models CS, CSU, CSUA, CSUA-PT, CSUAS, CSUAS-PT, CSUTD-D as well as associated accessories such as Model CSA and CSUATD-D and models with optional thermometer, PEX ends or ProPress ends.

  - Pre-approved equal.

2.02	COMPONENTS

- Thermostatic Balance Valve

- The valve shall be certified lead free according to NSF/ANSI 61 standards.

- The valve body shall be constructed out of stainless steel.

- The valve shall be rated for 200 PSIG working pressure and 250°F max. temperature.

- The valve shall have a fixed, non-adjustable (tamper-proof) temperature setpoint; temperature setpoints range from 80°F (27°C) to 170°F (27°C) in 5°F (2.8°C) increments.

- The valve shall have a temperature accuracy of ±3.0°F (±1.7°C).

- The valve shall have a wax thermostatic element.

- The valve shall come in 6 sizes: 1/2”; 3/4”; 1”; 1 1/4”; 1 1/2”; 2”.

2.02      ACCESSORIES

- Thermostatic Balance Valve Accessories

- Model CS and CSU with optional thermometer, PEX ends or ProPress ends.

- Model CSU, CSUA, CSUA-PT, CSUAS, CSUTD-D with integrated check valve.

- Model CSUA, CSUA-PT, CSUAS, and CSUAS-PT with shutoff valves and optional thermometer, PEX ends or ProPress ends.

PART 3 EXECUTION

  - INSTALLATION

- Install Thermostatic Balance Valve in accordance with manufacturer’s instructions.

- Unit shall be a ThermOmegaTech CircuitSolver® thermostatic balancing valve Models CS, CSU, CSUA, CSUA-PT, CSUAS, CSUAS-PT, CSUTD-D and associated assemblies CSA and CSUATD-D manufactured by ThermOmegaTech®, Warminster, PA.

###### END OF SECTION